## Slide 1
IP Paging: Make A Plan
Presented by:
Erich Bacher – Engineering Services Manager

## Slide 2
Agenda
Introductions
HBS Story
Emergency Communications Systems
Evaluating Existing Environment
Design Considerations
Implementation and Testing
Q and A
What are we going to accomplish here today?
Notes: ​

## Slide 3
Obligatory Hallway Image
Metacommentary about presentation tropes to establish rapport with audience

## Slide 4
Family Business
16 Years Voice Experience
Strengths in Troubleshooting and Project Management
Mitel, Cisco, Inter-tel, Panasonic, Samsung, Asterisk, 3Com
HP and Cisco Switching and Routing
Windows PC and Server
VMware
Security and Fire Alarms
Video Surveillance
Door Access
Structured Cabling
ALICE Certified
Photo Unavailable
Personal Background

## Slide 5
Kari’s Law
Kari’s Law applies to multi-line telephone systems (“MLTS”) installed” after
the compliance date of February 16, 2020. It requires:
REQUIRING A “PREFIX” WHEN CALLING 911:
Locations with MLTS must be able to dial 911 without an 8, 9 or other prefix.
ON-SITE NOTIFICATIONS:
When a 911 call is placed from an MLTS, a notification must be sent to on-site personnel, alerting them to the emergency. This can take the form of phone calls, visual alerts on a monitor, audible alarms, text messages, and/or emails.
RAY BAUM’s Act requires the FCC to consider rules to ensure that MLTS systems convey dispatchable address (defined as: “the street address of the calling party, and additional information such as room number, or similar information necessary to adequately identify the location of the calling party”) to public safety with a 911 call.
On August 2, 2019 the FCC released its Report and Order that adopted such rules and concluded its proceeding as directed by Section 506.
What does section 506 of RAY BAUM’s Act cover?
RAY BAUM’s Act requires that organizations with MLTS provide dispatchable location, i.e., street address, floor, room and/or suite number (if applicable) to public safety with 911 calls.
Ray Baum’s Act

## Slide 6
E911 Changes
Requirements In Effect Now – Kari’s Law
  Simply Dial 911
  Notify Onsite Staff
Requirements In Effect Soon™ – Ray Baum’s
  Provide Specific “Dispatchable” Location
  Analog telephone lines may not be adequate to meet requirements

## Slide 7
HBS
is a technology solutions provider specializing in information technology services. With 9 locations in the Midwest, HBS serves enterprise, public sector, and small and medium business with information technology services that provide business outcomes for our clients.

## Slide 8
Exceptional Value
Technology solutions aligned clients’ businesses
Our Clients
HBS intimacy with client's business. Vertical Focus – Public Sector, Commercial, SMB
Our People & Partners
The very best the in the industry.
Deliver exceptional value
to our clients through our great people and partners
Notes: We want to deliver and exceptional experience to our clients with our great people and partners.

## Slide 9
1990
2004
2005-2013
2018
2014-2017
Heartland is Born Alferi Communications provided labels to the grocery industry. Need for technology led to the creation of Heartland Business Systems.
Welcome Applications Team The World Wide Web proved the need for custom programming, website development and business intelligence.
Growth Heartland continues to expand by acquiring 10 companies and opens offices in Lisle, Illinois and Milwaukee, Wisconsin. We added Mitel and AV to our menu of services.
Present Day Heartland has 9 locations throughout the Midwest, 175+ Technical Professionals with over 500 industry certifications.
Expansion HBS opens offices in Minnesota and Iowa. We add Cloud, Managed Services, Imaging Services, Cybersecurity and Physical Security to our menu of services.
Our Proud History…
Notes: And over the years HBS has continued to invest in our client partnerships by growing our services portfolio and our footprint to continue to bring more value to our clients.

## Slide 10
Minneapolis
Appleton
Milwaukee
Madison
Eau Claire
Des Moines
Chicago
With a remarkable 25-year reputation with an unmatched service capability
600+ Employees Proudly Serving The Midwest
Who is HBS?:
Iowa City
Omaha
Notes: Today we offer the ability to serve our client in 9 locations and over 600 employees proudly partnering with clients throughout the Midwest with a remarkable 29 year history and an unmatched service capability.

## Slide 11
Emergency Communications Systems

## Slide 12
Emergency Communication Systems
Support one-way and two-way flow of emergency information
Commonly designed to convey over multiple media
Composed of input devices, sensors, and output devices
Handles both individual and group communications

## Slide 13
Emergency Communication Systems
An Effective ECS Should Be: Timely - Information must be able to reach entire audience quickly
Easy to Use - Emergencies make it difficult to remember instructions
Interoperable - Must work well within ecosystem of current and future systems
Multipath - Redundant methods of contact ensure audience is reached
Resilient - Must continue to operate under adverse conditions

## Slide 14
Emergency Communication Systems
Digital Signs
Mobile Radio
Desktop Notifications
Outdoor Loudspeakers
Mobile Devices
CCTV Override
Strobes & Beacons
Gate/Door Entry Buttons
IP Phones
IP Speakers / PA Systems
GPIO Contact Closures
LED Displays
Analog Systems
Email Alerts
Emergency Phones
SMS Messaging

## Slide 15
Evaluating the Existing Environment

## Slide 16
The Legacy

## Slide 17
Analog Paging - One Way, Centrally Amplified
Combined Speaker Wattage <= Amplifier Output Rating
25v or 70v are most common
Each zone is a single shared cable run.

## Slide 18
Analog Paging - One Way, Centrally Amplified
2.5w
Individual speakers can be “tapped” at different levels Volume adjustments require an engineer to rewire
2.5w
1.25w

## Slide 19
Analog Paging - One Way, Self Amplified
Most often 24v
Each zone is a single shared cable run.
Volume adjustments can be made at the device with a dial

## Slide 20
Analog Speakers - Talkback
Talkback Control Unit
Each speaker is its own zone and an individual cable run to the control equipment, not a parallel or daisy-chain Provides live audio monitoring of the area during an emergency situation.
25v and 45-ohm speakers are most common
Audio only uses one pair, similar to a phone line

## Slide 21
Analog Paging – Talkback Switch Panels

## Slide 22
Analog Speakers – Talkback Wiring

## Slide 23
Analog Speakers – Call Buttons

## Slide 24
Wait, what about that clock?

## Slide 25
Wired Synchronized Clocks
12v, 24v, or 110v are most common Clocks share single cable run, for the most part Synchronization is handled by tightly timed voltage application between leads. Each manufacturer has its own standard, but there is some inter-brand compatibility

## Slide 26
Wireless Synchronized Clocks
12v, 24v, or 110v are most common to power the devices Battery powered options Sync signaling is mostly proprietary, with little inter-brand compatibility

## Slide 27
IP POE Clocks
Powered by switching, each device independently able to get NTP. Completely standards-based.
Only downside is cost.

## Slide 28
We Can Just Page Over Our Phones
No, You Can’t.
Phone Speaker
Ceiling Speaker
Many phones don’t interrupt a call in-progress to receive a page
Phones aren’t placed in proper locations or loud enough
Many phone systems can’t page to all phones simultaneously
We Don’t Recommend It

## Slide 29
Where Are The Speakers?
Inventory each device, uniquely identify by room number HS-101-1
Note which IDF/MDF is closest
Solicit feedback from staff about nonfunctional speakers or areas of low sound
Keep an eye out for intentionally disabled speakers. Rag stuffed into horn casing, etc.
Does the speaker in place meet the needs of the environment?
* and clocks

## Slide 30
Design Considerations

## Slide 31
Where Should There Be Speakers?
We recommend providing clear, audible coverage to any room that is a teaching space, has students in it during the day, or any room where staff may be working in relative isolation.
Consider:
Restrooms
Stairways
Practice Rooms for Band and Choir – soundproofed?
Special Activity Rooms
Coaching areas and offices
Garage and Maintenance Areas
Outdoor areas that classes are brought
Courtyards
Evacuation Areas and Rally/Muster Points
Sporting Events, Tracks, and Stadiums
Rooftops
Fire Code Standard: Every physical space needs an annunciator.

## Slide 32
Is Audio The Right Way to Reach This Space?
Areas with high background noise may be best reached through visual means.
Signboards, strobes, or LEDs can indicate a page is in progress or communicate critical information.
Wood Shop
Metal Shop
Lunch Rooms
Pools
Band
Choir
Orchestra
“Anti Blast” systems can also dynamically increase the volume of sound output based on measured ambient noise levels.

## Slide 33
Device Alignment and Spacing
Sound moves, reflects, reverberates, and echoes.
More speakers, closer together and each at a lower volume will deliver the best clarity of sound.
Devices with strong directional sound– like horns – work best all pointed in the same direction.

## Slide 34
Zoning
Which areas of the building may need to be reached independently? Are there any events like bell schedules that need to reach some areas and not others?
Zones cannot be broken apart but can be combined together.

## Slide 35
Device Choices
Traditional Square or Circular Speakers Fit into existing spaces (measure on your walkthrough) May have integrated volume options Least costly, slower to install Installation location typically fixed

## Slide 36
Device Choices
Lay-In Ceiling Speakers Extremely fast installation, no mounting Great sound coverage and projection, excellent pickup from room Can be easily relocated, if extra cabling is left Hands down recommendation for best overall classrooms

## Slide 37
Device Choices
Wall Mounted Wall Mounted, recessed or surface mount Fairly directional sound Typically a smaller driver than lay-in ceiling tile, but good coverage Generally installed in a fixed position for its lifetime

## Slide 38
Device Choices
Speaker/Clock Combo Wall Mounted, recessed or surface mount
One device means fewer cables and switchports for IP endpoints Typically a smaller driver than lay-in ceiling tile, but good coverage Generally installed in a fixed position for its lifetime

## Slide 39
Device Choices
Clean Room Ceiling or Wall Mount Ideal for cafeteria areas where cooking oils in the air land on and reduce audio quality over time with traditional speakers.

## Slide 40
Device Choices
Horns Wall, Beam, or Fixed Ceiling Mounted
Great sound projection over distances Decent pickup for talkback, but not great. Hard to Damage All Weather

## Slide 41
What Is Already In Place to Tie Into the ECS?
Fire Alarms
Security Alarms
Mass Notification Email or SMS
Panic Buttons
Door Access Systems
Phone Systems
Two-way Radios
Weather Alert Radios
IOT – Monitor Defibrillators and Fire Extinguishers
IP Video Surveillance Systems
Digital Signage Systems
Wireless Pendant Systems
Temperature / Environmental Monitoring Systems

## Slide 42
Phone System Integration
If you can only initiate a page from the front office, this poses a serious bottleneck on timely communication, and a single point of failure in the event those staff aren’t able to make pages.
If it is not budgetarily feasible to address the broader system issues, investigate integration between the current paging system and current phone system.
It is important to consider with talkback capabilities that more than one page may occur at the same time. Plan for multiple connections and establish prioritization rules so the most urgent pages succeed when there is conflict.

## Slide 43
Phone System Integration
Absolutely crucial to the Inform directive of ALICE training

## Slide 44
Analog, IP, or Both
Analog Pros: Cost
IP Pros: Improved Sound Quality
Visibility / Supervision
Granularity Modularity
Ease of Management
Fits within IT Skillset
Enhanced Two-way Audio Simple Integration with Visual Alerting

## Slide 45
Analog, IP, or Both
Visibility –
Where are my speakers? Are they working?
Granularity –
Individual device level control of grouping, volume levels, and other settings
Modularity –
Adding or reallocating speakers is easy
Ease of Management –
IP based administration gives you full control over critical system
Fits within IT Skillset –
Installing or troubleshooting a speaker is like working with any other IP device

## Slide 46
Analog, IP, or Both
IP to Analog Gateways
Hybrid approach reduces cost
Can potentially reuse existing equipment and cabling*
Sacrifices endpoint visibility and granularity, generally for one-way devices in common areas
Documentation of cabling and device connections becomes critical to later troubleshooting
*easier said than done.

## Slide 47
IP Paging
Network Considerations
Most IP Paging systems use multicast to avoid excessive bandwidth during broadcasts. Multicast routing may be necessary between VLANs.
Isolate paging system in its own VLANs and limit access from student or guest accessible networks. Prioritize VLAN via QOS like other VOIP.
Unicast to Multicast bridges can be established where multicast routing isn’t ideal or possible.

## Slide 48
IP Paging
Switch Ports and Patch Panels
Keeping track of closest MDF/IDF during inventory will help Ensure you have enough
Vertical space for equipment
Cable management
Conduit dimensions
Patch cables

## Slide 49
Implementation and Testing

## Slide 50
Implementation
Document, Document, Document
Make sure your device inventory and floorplan always match when changes occur
Label devices with a unique number/naming scheme in a place that is visible from the ground.
Document which ethernet run and switchport serves which IP device.
Iterative numbering for analog devices chained together in a zone.

## Slide 51
Implementation
Alert
Consider utilizing panic buttons to quickly indicate school-wide that something has occurred. Position near secured ingress points and test usage regularly. Lockdown An ECS can provide real-time acknowledgement status information from classrooms. Talkback capabilities in each classroom are more important than ever to provide audio feedback about the situation in a room.
Inform Initiating a page should be easy to do (but not easy to accidentally do) from anywhere within the building in order to provide continual information on the developing situation Avoid the temptation to create commanding messaging. Challenge Disruptive tones and high volume, unexpected messaging can disrupt or confuse an attacker.
Evacuate
Ensure that the devices are positioned to communicate with students and staff once evacuated.

## Slide 52
Testing
Emergency systems MUST be regularly tested to ensure operational during an actual emergency
Daily Bells and Announcements are the best, easiest way to ensure good system health Utilize SNMP or other monitoring wherever possible and ensure errors and alerts will be escalated appropriately. Always respond to reports of poor communications on these day to day operations as if they had occurred during an emergency event.

## Slide 53
When Seconds Matter:
Network
Controls
National Weather Service and U.S. Dept. of Homeland Security
IP Gateway
Classroom, Common Area & Outside Speakers
IT AS THE CORE
Alert Notices & Conference Bridging
Ambulance
Police/Fire
Paging Amplifier
Principals
Teachers
Parents
Clocks, Security Cameras, Alarms & Locks
On Premise & Off Premise Notification

## Slide 54
Strategic Plan
In Person Interview
IT Synergy Survey
Process
Rough Order of Magnitude
Gap Analysis
Develop Target State
Document Current State
Identify Mission & Initiatives
1
2
3
4
5
Strategic Plan
In Person Interviews
Electronic Survey
Educational Goals
Architecture Review & Documentation
Data Collection
Future State Architecture Documentation
Future Educational Goals and Strategies
Execution Strategy
Current State – Future State
We are here!

## Slide 55
Evaluate Your Current System
Consider A Solution Design
Document Everything
Get it in the Budget
Call Me
Call Me

## Slide 56
Q&A

## Slide 57
Thank you for joining us today
Presented by:
Erich Bacher – Engineering Services Manager
ebacher@hbs.net
920.687.4684